## Slide 1
Uncertainties in Yield Assessments and PV LCOE
We moved forward from the uncertainty framework to real implementations of it and the impact that uncertainties can have on lifetime yield predictions, on the LCOE and on the cash flow.
The most important parameter influencing the energy yield assessment is the site-specific irradiation.
YA is not only about the software used, it is mainly about the user (personal experience, assumptions).
Seven highly skilled specialists did not arrive at the same result in the two benchmarking exercises
From an industry perspective, it would be beneficial if more “live” post-mortem analyses (i.e. comparison of the LTYP and measured data, every 5 years of system life) would be made and published.
Figure 16: Reduction of uncertainty
Figure 26: Post-mortem analysis
Figure 22: YA comparison
Report IEA-PVPS T13-18:2020, November 2020
Notes: To Topic 1: Several aspects need to be considered: reliability of the database, interannual varia-bility, long term trends.
To Topic 3: As seen from the YA exercises for Bolzano and Alice Springs, differences in these stem primarily from personal experience and assumptions by the modeler, of which
(i) the irradiance database selection and site adaptation (especially for mountainous terrain),
(ii) degradation/PLR assumption,
(iii) total modelling uncertainty values (as seen in the P50 and P90 ranges) and
(iv) soiling and far/near shading had the largest impact on the determined result.

## Slide 2
Uncertainties in Yield Assessments and PV LCOE
Possible issue: | Best practice
Estimation of correct site insolation | Check various sources of satellite data Ask satellite data provider for validated data with ground measurements Apply site adaptation
Long-term trend | Check the trend over different time-periods (.e.g 2011-2020, 2001-2010)
Transposition of GHI to GTI | Check in the literature which is the best combination of decomposition and transposition models for the specific climate Check for consistency in the % contribution by using various irradiance sources
Parameterization of components (PV Modules, Inverters) | Check reliability of provided files, ask manufacturer for qualified data
Shading | In case of far shading check the sensitivity of the yield on different hourly profiles
Soiling | In case of measurements, evaluate non-uniformity over the selected site
Temperature effects | Check various sources of satellite data Ask satellite data provider for validated data with ground measurements
Performance Loss Rates | Make sure that one includes not only module degradation and that also unavailability and reversible failures are considered
Calculation of uncertainty | Use semi-empirical calculation methods if long-term data is available and distribution deviates from normal (gaussian)
O&M costs in business models | Based the assumptions on real cost data and not on a % of CAPEX
Report IEA-PVPS T13-18:2020, November 2020